1.0 - General

1.1 – Roomside replaceable ducted ceiling module with sealed air entry chamber, air volume control, and 40% open area face grille.

1.2 – Sizes shall be as noted on drawings or other supporting materials.

2.0 - Construction

2.1 - Filter hood shall be constructed of (0.063" aluminum, 16 gauge 304/L or 316/L stainless steel) with joints and seams factory welded.  Hoods shall be designed in such a manner that they are 100% seal welded at the pressure boundary of the filter-to-hood interface; i.e., silastic sealants are not allowed as a means of sealing the upstream side of the hood from the cleanroom.

2.2 - Hood design shall include an integral knife-edge on the inside perimeter of housing-to-filter seal. A fluid gel shall be used to seal the filters to the hood knife-edge. Hoods shall include spring loaded filter guides to self-center filter onto hood knife-edge and provide temporary installation of the filter. The filter shall be secured to the knife edge utilizing tool less filter clamps.  Hood shall be designed such that one personnel can remove and install the filter without the use of tools.

2.3 - Hood shall be provided with a flush hinged removable perforated T-304 stainless steel grille having 40% open area with 2B finish. The grille shall have concealed hinges and be hinged on the long side and retained by two concealed stainless steel grill quick fasteners, which shall not require the use of hand tools for filter service.

2.4 - Hood shall include a diffuser plate on the air inlet, to diffuse the air throughout the plenum area above the filter, providing uniform air distribution through the filter in accordance with IEST-RP-C0034.3. See note 2.4a.

2.5 - Hood shall have a sample port accessible from room side. The port shall sample the upstream side of the installed filter in order to determine pressure drop across the filter as well as the upstream challenge aerosol concentration. Sample port shall be a 3/8" NPT chrome plated brass quick-disconnect with integral spring loaded shut off valve with a snap-in barbed connector. See note 2.5a, page 8.

2.6 - Hood shall have a rigid metal injection nozzle accessible from the room side to inject an aerosol challenge into the unit’s upstream plenum for testing. The injection nozzle shall radially disperse the aerosol challenge to provide uniform mixing in accordance with IEST-RP-C0034.3.  The aerosol injection connection shall be a 3/8" coupling welded in place with a 3/8” NPT chrome plated brass quick-disconnect with integrated shut off valve.

2.7 – A guillotine type damper shall have two (2) blades, which slide horizontally from open to close. Damper adjustments shall be fully accessible from the room side. The damper control rod shall be operated by means of a 9/16" nut driver/socket or ratchet/socket. Damper shall be operated by a mechanical linkage and be factory installed. It shall have a positive locking feature and a damper position indicator.

2.8 –Stainless Permanent trim (SPT) shall be a (5/8", 1-1/2, 2”) trim fabricated of 14-gauge T-304 or 316 stainless steel with a #3 finish on the room side surface. The SPT trim shall be factory installed and attached to the hood body with stainless steel pop rivets without penetrating the hood’s pressure boundary. See note 2.8a.

(2.8 - Stainless Removable Trim (SRT) shall be (1-1/2", 2") wide trim fabricated of 14-gauge T-304 or 316 stainless steel with a #3 finish on the room side surface. The design of the hood shall allow the SRT to be field attached to the hood body with stainless steel pop rivets without penetrating the hood’s pressure boundary. Outside comers shall have a 1/8" radius to help prevent injuries during installation.) See note 2.8b.

2.9 - Hood shall have a duct connection collar which shall extend a minimum of 3" from the top surface of the hood. Collars shall have a raised rib or duct grips to prevent flex duct blow-off and shall be fully welded to the hood body.  See note 2.9a.

(2.10 - Hood shall be insulated externally on (both top and sides, top only), with 2" thick foil back insulation held in place with 3" aluminum foil tape and insulation hangers.)

2.11 – Hood shall have integrated hanging receiver clips that accept a universal hanging bracket.  Universal hanging bracket shall be designed such that it allows three different installation options for the hood; suspension by threaded rod, suspension by wire, and compression to ceiling substrate.

3.0 – Performance

3.1 - All hood welds will be visually inspected for pinholes, porosity, indentations or inclusions exceeding 10% of base metal; lack of filler material, excessive weld build up and cold shunts.

3.2 - Hood shall be leak tested per defined quality control procedure, Camfil # CFWSP-5001. The hood knife-edge shall be sealed off with a jig and the hood plenum area will be pressurized to 3.0" w.g. All welds in the knife-edge area and all penetrations such as damper control, static and aerosol ports, shall be bubble-tested for leaks. The exterior hood body welds shall also be bubble-leak tested. All hoods must meet zero leak criteria before shipping from the factory.

3.3 – Each unit shall be individually serialized and traceable to the aforementioned leak test procedure.

3.4 – Manufacturer shall provide qualification reports certifying that the hoods meet IEST-RP-C034.3 for airflow and aerosol uniformity.

3.4 - Manufacturer shall provide evidence of facility certification to ISO 9001:2008.

4.0 – Transport

4.1 - After the hood has been found acceptable, it shall be cleaned and packaged for shipping. Hoods with trims larger than 5/8" will be boxed with foam spacer blocks to prevent damage to trim.

Modules shall be Camfil PharmaSeal Gen II.

Optional items in parentheses ( ) require selection.

Notes:

2.4a - Hoods used in exhaust applications shall not have a diffuser plate.

2.5a - Barbed connections for hoods, quantity required (shipped separately): 1 set of 2 barbed connectors for up to 50 hoods, 2 sets of barbed connectors for 51 to 150 hoods, and 3 sets of barbed connectors for more than 150 hoods.

2.8a – The 5/8” width SPT trim is commonly used in 1-1/2 or heavy-duty T-bar applications and is factory installed.

2.8b - This type of trim is commonly used for hard/plaster ceilings.

2.9a - 4” for bubble tight dampers. Square inlets shall have a 1-1/2 wide flange.